## DATA TRANSFER
Unity_DS3D (CPU_WS)
Unity INPUTS from DS3D | [6 empty] | OUTPUT TO DS3D | [7 empty] | TO UNITY
SR.No | Variable | Labels | Units | Data Type | Value | Remark | SR.No | Variable | Labels | Units | Data Type | Value | Remark | Do not touch | Requirement | Remarks
1 | Active_Fault_Status | Active Fault Status | Code | Integer | 1 | If Fault is active: 1, Fault Inactive: 0 | 1 | BlueArrowOut | Fresh Air arrow | Fresh Air blue arrow | Integer | 5 | 0-10 (Speed) |  | Every Arrow with Speed
2 | Current_Step_Number | Current Step Number | Step | Integer | 1 | 1-based step index in procedure (0 = reset/unstarted) | 2 | Fan1 | Condensor Fan RedArrow Set 1 | Condensor Fan RedArrow Set 1 | Integer | 5 | 0-10 (Speed) |  | Every Arrow Colour Control
3 | Total_Steps | Total Steps in Procedure | Steps | Integer | 15 | Total steps for active fault | 3 | Fan2 | Evaporator Fan RedArrow Set 2 | Evaporator Fan RedArrow Set 2 | Integer | 5 | 0-10 (Speed) |  | Application Quit
4 | Wrong_Attempts | Wrong Attempts Counter | Count | Integer | 0 | Total number of times wrong steps were taken | 4 | GreenArrowIN1 | Fresh Air Damper Right | Fresh Air Damper Right | Integer | 0 | 0-10 (Speed) |  | Fresh Air Damper Left Position
5 | Fault_101_Status | Fault 101: No HVAC operations | State | Boolean | 0 | 0: Inactive, 1: Active (14 steps) | 5 | GreenArrowIN2 | Fresh Air Damper left | Fresh Air Damper left | Integer | 0 | 0-10 (Speed) |  | Fresh Air Damper Right Position
6 | Fault_102_Status | Fault 102: No ventilation | State | Boolean | 0 | 0: Inactive, 1: Active (22 steps) | 6 | YellowArrowIn | Return Air Damper | Return Air Damper | Integer | 5 | 0-10 (Speed) |  | Return Air Damper Position
7 | Fault_103_Status | Fault 103: Reduced ventilation | State | Boolean | 0 | 0: Inactive, 1: Active (15 steps) | 7 | RedArrow_Inlet | Fresh Air arrow Colour | Intensity | Float | 0 | 0: Red, 1: Green, 2: Yellow, 3: Blue |  | Fault Code | Code to trigger the repective fault on Unity
8 | Fault_104_Status | Fault 104: Suction low and discharge low (C1) | State | Boolean | 1 | 0: Inactive, 1: Active (15 steps) | 8 | RedArrow_Outlet | Condensor Fan RedArrow Set 1 Colour | Intensity | Float | 0 | 0: Red, 1: Green, 2: Yellow, 3: Blue |  | Fault Reset Trigger | Boolean in Excel toReset Entire Screen to Normal Mode
9 | Fault_105_Status | Fault 105: Suction low and discharge low (C2) | State | Boolean | 0 | 0: Inactive, 1: Active (14 steps) | 9 | BlueArrow_Outlet | Evaporator Fan RedArrow Set 2 Colour | Intensity | Float | 0 | 0: Red, 1: Green, 2: Yellow, 3: Blue |  | Show Hide Objects
10 | Fault_106_Status | Fault 106: High suction and high discharge | State | Boolean | 0 | 0: Inactive, 1: Active (26 steps) | 10 | GreenArrow_Inlet | Fresh Air Inlet Color Intensity | Intensity | Float | 0 | 0-10 (Material color lerp) |  | All Component Highlight | As per discussion
11 | Fault_107_Status | Fault 107: Compressor not operating | State | Boolean | 0 | 0: Inactive, 1: Active (40 steps) | 11 | YellowArrow_Inlet | Return Air Inlet Color Intensity | Intensity | Float | 0 | 0-10 (Material color lerp)
12 | Fault_108_Status | Fault 108: Reduced cooling | State | Boolean | 0 | 0: Inactive, 1: Active (33 steps) | 12 | FADL | Fresh Air Damper Left Position | Position | Float | 0 | %
13 | Fault_109_Status | Fault 109: No Heating | State | Boolean | 0 | 0: Inactive, 1: Active (15 steps) | 13 | FADR | Fresh Air Damper Right Position | Position | Float | 0 | %
14 | Fault_110_Status | Fault 110: Over Cooling | State | Boolean | 0 | 0: Inactive, 1: Active (8 steps) | 14 | RAD | Return Air Damper Position | Position | Float | 0 | 0 &100%
15 | Fault_111_Status | Fault 111: Over Heating | State | Boolean | 0 | 0: Inactive, 1: Active (7 steps) | 15 | DS3D_OFF | DS3D Application Quit | DS3D OFF | Integer | 0 | 0: Running, 1: Shutdown
16 | Fault_112_Status | Fault 112: No emergency ventilation | State | Boolean | 0 | 0: Inactive, 1: Active (14 steps) | 16 | Fault_Code_Trigger | Fault Trigger Scenario Code | Code | Integer | 104 | Active Fault to Unity (101-114 active)
17 | Fault_113_Status | Fault 113: Smoke identified in saloon | State | Boolean | 0 | 0: Inactive, 1: Active (13 steps) | 17 | Fault_reset | Fault Reset Trigger | Command | Integer | 0 | 0: Idle, 1: Reset
18 | Fault_114_Status | Fault 114: Compressor / Blower noisy | State | Boolean | 0 | 0: Inactive, 1: Active (36 steps) | 18 | ShowHideObjects | Toggle Component Visibility | State | Boolean | 0 | 0: Hide, 1: Show
19 | Fault_115_Status | Fault 115: Spare Fault Scenario | State | Boolean | 0 | 0: Inactive, 1: Active (Reserved in Excel) | 19 | Compresor 1_Highlights | Toggle Compressor Highlights Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights
20 | Fault_116_Status | Fault 116: Spare Fault Scenario | State | Boolean | 0 | 0: Inactive, 1: Active (Reserved in Excel) | 20 | Compresor 2_Highlights | Toggle Compressor Highlights Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights
21 |  | Spare |  | Boolean |  |  | 21 | Compresor 3_Highlights | Toggle Compressor Highlights Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights
22 |  | Spare |  | Boolean |  |  | 22 | Compresor 4_Highlights | Toggle Compressor Highlights Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights
23 |  | Spare |  | Boolean |  |  | 23 | FAT_Sensor_Highlights | Toggle FAT Sensor Highlight Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights (Fresh Air Temp)
24 |  | Spare |  | Boolean |  |  | 24 | RAT_Sensor_Highlights | Toggle RAT Sensor Highlight Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights (Return Air Temp)
25 |  | Spare |  | Boolean |  |  | 25 | SAT_Sensor_Highlights | Toggle SAT Sensor Highlight Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights (Supply Air Temp)
26 |  | Spare |  | Boolean |  |  | 26 | Smoke_Detector_Highlights | Toggle Smoke Detector Highlight Visibility | State | Boolean | 1 | 0: Hide Highlights, 1: Show Highlights (Smoke Detector)
27 |  | Spare |  | Boolean |  |  | 27 | Spare Sensor | Spare |  | Integer | 0
28 |  | Spare |  | Boolean |  |  | 28 | Spare Sensor | Spare |  | Integer | 0
29 |  | Spare |  | Boolean |  |  | 29 |  | Spare |  | Integer | 0
30 |  | Spare |  | Boolean |  |  | 30 |  | Spare |  | Integer | 0
31 |  | Spare |  | Boolean |  |  | 31 |  | Spare |  | Integer | 0
32 |  | Spare |  | Boolean |  |  | 32 |  | Spare |  | Integer | 0
33 |  | Spare |  | Boolean |  |  | 33 |  | Spare |  | Integer | 0
34 | Telemetry_Event | Telemetry Event Name | String | String | fault_started | fault_started / step_completed / fault_completed | 34 |  | Spare |  | Integer | 0
[7 empty] | 35 |  | Spare |  | Integer | 0
[7 empty] | 36 |  | Spare |  | Integer | 0
[7 empty] | 37 |  | Spare |  | Integer | 0
[7 empty] | 38 |  | Spare |  | Integer | 0
[7 empty] | 39 |  | Spare |  | Integer | 0
[7 empty] | 40 |  | Spare |  | Integer | 0
[7 empty] | 41 |  | Spare |  | Integer | 0
[7 empty] | 42 |  | Spare |  | Integer | 0
[7 empty] | 43 |  | Spare |  | Integer | 0
[7 empty] | 44 |  | Spare |  | Integer | 0
[7 empty] | 45 |  | Spare |  | Integer | 0
[7 empty] | 46 |  | Spare |  | Integer | 0
[7 empty] | 47 |  | Spare |  | Integer | 0
[7 empty] | 48 |  | Spare |  | Integer | 0
[7 empty] | 49 |  | Spare |  | Integer | 0

## Fault Logic
Components | Status | Fault 101 | No HVAC Operation | Steps Complete | 4 | Fault 102 | No Ventilation | Steps Complete | 0 | Fault 103 | Reduced Ventilation | Steps Complete | 8 | Fault 104 | Suction low and discharge low | Steps Complete | 1 | Fault 105 | Suction low and discharge low | Steps Complete | 8 | Fault 106 | High suction and high discharge | Steps Complete | 8 | Fault 107 | Compressor not Operating | Steps Complete | 8 | Fault 108 | Reduced Cooling | Steps Complete | 8 | Fault 109 | No Heating | Steps Complete | 8 | Fault 110 | Overcooling | Steps Complete | 8 | Fault 111 | Overheating | Steps Complete | 8 | Fault 112 | No Emergency Ventilation | Steps Complete | 8 | Fault 113 | Smoke Identified in Saloon | Steps Complete | 8 | Fault 114 | Compressor is excessively noisy ¦ Condenser Fan or Supply air Blower is excessively noisy ¦ Noisy TX valve ¦ HVAC unit is noisy | Steps Complete | 2
HVAC OFF |  | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered | Cause 1 |  |  | Cause Triggered
Control Panel Circuit Breakers |  | Cause 2 |  |  | 1 | Cause 2 |  |  | 1 | Cause 2 |  |  | 0 | Cause 2 |  |  | 1 | Cause 2 |  |  | 0 | Cause 2 |  |  | 0 | Cause 2 |  |  | 0 | Cause 2 |  |  | 0 | Cause 2 |  |  | 0 |  |  |  | 0 | Cause 2 |  |  | 0 |  |  |  | 0 | Cause 2 |  |  | 0 | Cause 2 |  |  | 0
Supply Air Fan | [5 empty] | Cause 3 |  |  |  | Cause 3 | Refrigerant Leak | [10 empty] | Cause 3 |  |  |  | Cause 3 |  |  |  | Cause 3 |  |  |  | Cause 3 | [19 empty] | Cause 3
|  | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Cause 4 |  |  |  | Sr No | Fault Step | Step Status | Remarks | Cause 4 |  |  |  | Cause 4 |  |  |  | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Sr No | Fault Step | Step Status | Remarks | Cause 4
Compressor | 1 | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Remove Condenser Mesh with lifting device (Lifting Device) |  | 1: Complete, 0: Incomplete | Sr No | Fault Step | Step Status | Remarks | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | Cause 5 |  |  |  | Cause 5 |  |  |  | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete | Cause 5
Supply Air Fan Circuit |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove Condenser Coil & Filter with lifting device (Lifting Device) |  |  | 1 | Unscrew Fan cover bolt (Spanner) |  | 1: Complete, 0: Incomplete |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  | Cause 6 |  |  |  | Sr No | Fault Step | Step Status | Remarks |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  | Cause 6
Supply Air Filter |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Check for leaks using Electronic leak detector (Electronic Leak Detector) |  |  |  | Open fan cover (Insulated Gloves) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  | Sr No | Fault Step | Step Status | Remarks | 1 | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  | 1: Complete, 0: Incomplete |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  | Cause 7
Evaporator Coil Damage |  |  | Remove electrical control panel assembly (Spanner) |  |  |  | Remove electrical control panel assembly (Spanner) |  |  |  | Open supply air blower (Spanner) |  |  |  | Check the evaporator coil (1) for any damages to the fins. (Visual Inspection Lamp) |  |  |  | Open Filter Drier Cover (Screwdriver) |  |  |  | Unscrews Fan Motor Bolt (Spanner) |  |  |  | Remove electrical control panel assembly (Spanner) |  |  | 1 | Unscrew bottom panel (Spanner) |  | 1: Complete, 0: Incomplete |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Open supply air cover (Spanner) |  |  |  | Check the temperature sensors for any damage (Clamp Thermometer) |  |  |  | Remove electrical control panel assembly (Spanner) |  |  |  | Remove the fresh air dampers (Spanner) |  |  | Cause 8
TX Valve |  |  | Check all circuit breakers and close. (Multimeter) |  |  |  | Check all circuit breakers and close. (Multimeter) |  |  |  | Clean the supply air blower (1) with compressed air. (Compressed Air Gun) |  |  |  | Check and defrost evaporator coil. (Visual Inspection) |  |  |  | Remove Filter Drier (Insulated Gloves) |  |  |  | Remove Fan Motor (Insulated Gloves) |  |  |  | Check all circuit breakers and close. (Multimeter) |  |  |  | Remove bottom panel (Insulated Gloves) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Remove FAT Bolt (Spanner) |  |  |  | RAT Damaged (Visual Inspection) |  |  |  | Check all circuit breakers and close. (Multimeter) |  |  |  | Replace the fresh air dampers (Visual Inspection) |  |  | Cause 9
Filter Drier |  |  | Unplug the connected wires (Screwdriver) |  |  |  | Unplug the connected wires (Screwdriver) |  |  |  | Rotate supply air blower (1) motor with hand and ensure that only a light force is required to rotate it. (Insulated Hand Gloves) |  |  |  | Use a fin comb to straighten any bent fins. (Fin Comb) |  |  |  | Replace Filter Drier (None) |  |  |  | Replace Fan Motor (None) |  |  |  | Unplug the connected wires (Screwdriver) |  |  |  | Unscrew return air damper (Spanner) |  |  |  | Remove electrical control panel assembly (Spanner) |  |  |  | Replace with new FAT Sensor (None) |  |  |  | Unbolt the return air temperature sensor (Spanner) |  |  |  | Unplug the connected wires (Screwdriver) |  |  |  | Unscrew fresh air filter bolt (Screwdriver) |  |  | Sr No | Fault Step | Step Status | Remarks
Condensor Fan Motor |  |  | Remove electrical plugs. (Insulated Gloves) |  |  |  | Remove electrical plugs. (Insulated Gloves) |  |  |  | Remove supply air blower (Screwdriver) |  |  |  | Wash the evaporator coil (1) with warm to hot water and a small quantity of detergent. The hot water softens the bristles helps the grease to dissolve and removes the chlorides. (Bristle Brush) |  |  |  | Check LP/HP (Manifold Gauge Set) |  |  |  | Clean the condenser fan with dry compressed air (Compressed Air) |  |  |  | Remove electrical plugs. (Insulated Gloves) |  |  |  | Remove return air damper (Insulated Gloves) |  |  |  | Check all circuit breakers and close. (Multimeter) |  |  |  | Secure with FAT bolt (None) |  |  |  | Remove the return air temperature sensor (None) |  |  |  | Remove electrical plugs. (Insulated Gloves) |  |  |  | Replace fresh air filter (Visual Inspection) |  |  | 1 | Run HVAC 20 mins. (None) |  | 1: Complete, 0: Incomplete
Condensor Fan Circuit Breaker |  |  | Replace the plugs (Visual Inspection) |  |  |  | Replace the plugs (Visual Inspection) |  |  |  | Replace supply air blower (Visual Inspection) |  |  |  | Clean the drain tray (2) with wet cloth (Wet Cloth) |  |  |  | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  |  |  | Unscrew condenser fan bolt (Spanner) |  |  |  | Replace the plugs (Visual Inspection) |  |  |  | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  |  |  | Unplug the connected wires (Screwdriver) |  |  |  | Remove SAT Bolt (Spanner) |  |  |  | Replace the return air temperature sensor (None) |  |  |  | Replace the plugs (Visual Inspection) |  |  |  | Remove fresh air damper motor (Screwdriver) |  |  |  | Unusual noise from compressor assembly (None)
Condensor Coil |  |  | Connect the electrical plugs. (Screwdriver) |  |  |  | Connect the electrical plugs. (Screwdriver) |  |  |  | Close air supply blower (Visual Inspection) |  |  |  | Ensure that there is no condensate or debris left over on the drain tray (2). (Vacuum Cleaner) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove condenser fan (Insulated Gloves) |  |  |  | Connect the electrical plugs. (Screwdriver) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Remove electrical plugs. (Insulated Gloves) |  |  |  | Remove SAT Sensor (None) |  |  |  | Secure the RAT sensor bolt (None) |  |  |  | Connect the electrical plugs. (Screwdriver) |  |  |  | Replace fresh air damper motor (Visual Inspection) |  |  |  | Unscrew bolt compressor unit cover (Spanner)
Refrigerent Level |  |  | Close electrical control panel assembly (None) |  |  |  | Close electrical control panel assembly (None) |  |  |  | Unscrew bottom panel (Spanner) |  |  |  | Remove the grommet on the drain hole cover. (Pliers) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Replace condenser fan (None) |  |  |  | Close electrical control panel assembly (None) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Replace the plugs (Visual Inspection) |  |  |  | Replace with new SAT Sensor (None) |  |  |  | Tighten the fastener of RAT (Spanner) |  |  |  | Close electrical control panel assembly (None) |  |  |  | Clean Smoke Detector (Bristle Brush) |  |  |  | Compressor Cover Removal (None)
RAT Sensor |  |  | Open supply air cover (Spanner) |  |  |  | Open supply air blower (Spanner) |  |  |  | Remove bottom panel (Insulated Gloves) |  |  |  | Place the hose inside the hole and use high pressure to remove the debris from the drain hole. (None) |  |  |  | Check temperature of solenoid valve using clamp thermometer (Clamp Thermometer) |  |  |  | Remove the condenser coil cover (Lifting Device) |  |  |  | Unscrew bolt compressor unit cover (Spanner) |  |  |  | Remove Heat bank screws (Spanner) |  |  |  | Tighten loose connection of circuit breakers (Screwdriver) |  |  |  | Secure with SAT Bolt (None) |  |  |  | Check working (Visual Inspection) |  |  |  | DB9 Connection Clarification Pending (None) |  |  |  | Remove Smoke Detector Bolts (Spanner) |  |  |  | Check hp lp pressure using manifold gauge set (None)
Evaporator Coil |  |  | Clean the supply air cover (1) with compressed air. (Compressed Air Gun) |  |  |  | Clean the supply air blower (1) with compressed air. (Compressed Air Gun) |  |  |  | Unscrew return air damper (Spanner) |  |  |  | Ensure that draining is done completely through the drain tube (3). (Compressed Air Gun) |  |  |  | Unscrew solenoid valve using spanner (Spanner) |  |  |  | Clean condenser coil (Bristle Brush) |  |  |  | Compressor Cover Removal (None) |  |  |  | Remove Heat bank assembly (Insulated Gloves) |  |  |  | Circuit Breaker Cleaning (Bristle Brush) |  |  |  | Unbolt the return air temperature sensor (Spanner) | [7 empty] | Remove Converter Bolts (Spanner) |  |  |  | Remove Smoke Detector unit (Visual Inspection) |  |  |  | Unscrew compressor bolt (Spanner)
Condensor Coil |  |  | Rotate supply air cover (1) motor with hand and ensure that only a light force is required to rotate it. (Insulated Hand Gloves) |  |  |  | Rotate supply air blower (1) motor with hand and ensure that only a light force is required to rotate it. (Insulated Hand Gloves) |  |  |  | Remove return air damper (Insulated Gloves) |  |  |  | Check for leaks in TX Valve (Electronic Leak Detector) |  |  |  | Remove solenoid valve (Visual Inspection) |  |  |  | Straighten any bent fins with a fin comb (Fin Comb) |  |  |  | Clean the dust on the component with a soft bristle brush (with the metal part insulated) (Bristle Brush) |  |  |  | Replace Heat bank assembly (None) |  |  |  | Close electrical control panel assembly (None) |  |  |  | Remove the return air temperature sensor (None) | [7 empty] | Converter Removal (Lifting Device) |  |  |  | Replace Smoke Detector unit (Visual Inspection) |  |  |  | Remove the compressor (Insulated Gloves)
Solenoid Valve |  |  | Remove supply air blower (Screwdriver) |  |  |  | Remove supply air blower (Screwdriver) |  |  |  | Check moisture indicator on the sight glass (1) to find any excessive moisture in the system. (Electronic Leak Detector) |  |  |  | Fix TX valve with spanner (Spanner) |  |  |  | Replace solenoid valve (Visual Inspection) |  |  |  | Clean the coil with compressed air (Compressed Air) |  |  |  | Ensure compressor is not over heated (Clamp Thermometer) |  |  |  | Use a fin comb to straighten any bent fins. (Fin Comb) |  |  |  | Check Heat Bank (Clamp Thermometer) |  |  |  | Replace the return air temperature sensor (None) |  |  | Sr. No. | Components Affected |  |  |  | Check for short circuit using multimeter (Visual Inspection) |  |  |  | Secure Smoke Detector Bolts (None) |  |  |  | Replace the compressor (None)
Heater |  |  | Replace supply air blower (Visual Inspection) |  |  |  | Replace supply air blower (Visual Inspection) |  |  |  | Locate the leak (Spanner) |  |  |  | Remove TX valve if necessary (Visual Inspection) |  |  |  | Screw solenoid valve using spanner (Visual Inspection) |  |  |  | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  |  |  | Unscrew Fan bolt (Spanner) |  |  |  | Wash the evaporator coil (1) with warm to hot water and a small quantity of detergent. The hot water softens the bristles helps the grease to dissolve and removes the chlorides. (Bristle Brush) |  |  |  | Heat bank damaged (None) |  |  |  | Secure the RAT sensor bolt (None) |  |  | 1 | RAT Sensor |  | Open: 1, Close: 0 |  | Put converter back to it place (Visual Inspection) |  |  |  | Check working (Visual Inspection) |  |  |  | Compressor Cover close (None)
Electrical Connections |  |  | Check working (Visual Inspection) |  |  |  | Close air supply blower (Visual Inspection) |  |  |  | Repair the leak (None) |  |  |  | Replace TX valve if necessary (Visual Inspection) |  |  |  | Check HVAC working (Visual Inspection) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Open fan cover (Insulated Gloves) |  |  |  | Clean the drain tray (2) with wet cloth (Wet Cloth) |  |  |  | Remove Heat bank screws (Spanner) |  |  |  | Tighten the fastener of RAT (Spanner) |  |  | 2 | HOT 1 Switch |  |  |  | Secure converter with bolts (Visual Inspection) | [7 empty] | Screw bolt compressor unit cover (None)
Temperature Sensor | [6 empty] | Unscrew fresh air filter bolt (Screwdriver) |  |  |  | Check working (Visual Inspection) |  |  |  | Check working (Visual Inspection) | [7 empty] | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Unscrews Fan Motor Bolt (Spanner) |  |  |  | Ensure that there is no condensate or debris left over on the drain tray (2). (Vacuum Cleaner) |  |  |  | Remove Heat bank assembly (Insulated Gloves) |  |  |  | Check working (Visual Inspection) | [7 empty] | Check working (Visual Inspection) | [7 empty] | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner)
RAT Sensor | [6 empty] | Replace fresh air filter (Visual Inspection) | [15 empty] | Open supply air blower (Spanner) |  |  |  | Remove Fan Motor (Insulated Gloves) |  |  |  | Remove the grommet on the drain hole cover. (Pliers) |  |  |  | Replace Heat bank assembly (None) | [7 empty] | Cause 1 & Rectified | [6 empty] | Sr. No. | Components Affected |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers)
Smoke Detector |  | Sr. No. | Components Affected | Status | Remarks |  | Clean the fresh air dampers (1) and damper motor (2) with dry compressed air. (Bristle Brush) | [10 empty] | Sr. No. | Components Affected |  |  |  | Clean the supply air blower (1) with compressed air. (Compressed Air Gun) |  |  |  | Replace Fan Motor (None) |  |  |  | Place the hose inside the hole and use high pressure to remove the debris from the drain hole. (None) |  |  |  | Clean Heat bank (Compressed Air Gun) | [7 empty] | Cause 2 & Rectified |  | Not present |  |  |  |  | 1 | Fresh Air Damper |  | Open: 1, Close: 0 |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None)
|  | 1 | Control Panel Circuit Breakers |  | Open: 1, Close: 0 |  | Remove the fresh air dampers (Spanner) |  |  | Sr. No. | Components Affected |  |  | Sr. No. | Components Affected |  |  | 1 | Filter Drier |  | Open: 1, Close: 0 |  | Rotate supply air blower (1) motor with hand and ensure that only a light force is required to rotate it. (Insulated Hand Gloves) |  |  |  | Clean the condenser fan with dry compressed air (Compressed Air) |  |  |  | Fix TX valve with spanner (Spanner) |  |  |  | Unbolt the return air temperature sensor (Spanner) |  |  | Sr. No. | Components Affected |  |  |  | Fault Reset Logic |  |  | Sr. No. | Components Affected |  |  | 2 | Smoke Detector |  |  |  | Remove electrical control panel assembly (Spanner)
|  |  | Supply Air Blower |  |  |  | Replace the fresh air dampers (Visual Inspection) |  |  | 1 | Supply Air Filter |  | Open: 1, Close: 0 | 1 | Evaporator Coil Damage |  | Open: 1, Close: 0 | 2 | Piping Section |  |  |  | Remove supply air blower (Screwdriver) |  |  |  | Unscrew condenser fan bolt (Spanner) |  |  |  | Remove TX valve if necessary (Visual Inspection) |  |  |  | Remove the return air temperature sensor (None) |  |  | 1 | Temperature Sensor |  | Open: 1, Close: 0 |  |  |  |  | 1 | Electrical Connections |  | Open: 1, Close: 0 | [5 empty] | Check all circuit breakers and close. (Multimeter)
[7 empty] | Remove fresh air damper motor (Screwdriver) |  |  |  | Supply Air Blower |  |  | 2 | TX Valve | [7 empty] | Replace supply air blower (Visual Inspection) |  |  |  | Remove condenser fan (Insulated Gloves) |  |  |  | Replace TX valve if necessary (Visual Inspection) |  |  |  | Replace the return air temperature sensor (None) | [15 empty] | Cause 1 & Rectified |  |  |  | Unplug the connected wires (Screwdriver)
|  |  | Cause 1 & Rectified |  |  |  | Replace fresh air damper motor (Visual Inspection) |  |  |  | Refrigerent Level | [11 empty] | Close air supply blower (Visual Inspection) |  |  |  | Replace condenser fan (None) |  |  |  | Remove the condenser coil cover (Lifting Device) |  |  |  | Bolt the RAT (None) |  |  |  | Cause 1 & Rectified | [7 empty] | Cause 1 & Rectified |  |  |  | Cause 2 & Rectified |  |  |  | Remove electrical plugs. (Insulated Gloves)
|  |  | Cause 2 & Rectified |  |  |  | Check working (Visual Inspection) | [11 empty] | Cause 1 & Rectified |  |  |  | Unscrew bottom panel (Spanner) |  |  |  | Remove the condenser coil cover (Lifting Device) |  |  |  | Clean condenser coil (Bristle Brush) |  |  |  | Check working (Visual Inspection) |  |  |  | Fault Reset Logic | [7 empty] | Fault Reset Logic |  |  |  | Fault Reset Logic |  |  |  | Replace the plugs (Visual Inspection)
|  |  | Fault Reset Logic |  | 1: Reset | [5 empty] | Cause 1 & Rectified |  |  |  | Cause 1 & Rectified |  |  |  | Cause 2 & Rectified |  |  |  | Remove bottom panel (Insulated Gloves) |  |  |  | Clean condenser coil (Bristle Brush) |  |  |  | Straighten any bent fins with a fin comb (Fin Comb) | [23 empty] | Connect the electrical plugs. (Screwdriver)
[11 empty] | Cause 2 & Rectified |  |  |  | Cause 2 & Rectified |  |  |  | Fault Reset Logic |  |  |  | Unscrew return air damper (Spanner) |  |  |  | Straighten any bent fins with a fin comb (Fin Comb) |  |  |  | Clean the coil with compressed air (Compressed Air) | [23 empty] | Close electrical control panel assembly (None)
[6 empty] | Sr. No. | Components Affected |  |  |  | Cause 3 & Rectified |  |  |  | Fault Reset Logic | [7 empty] | Remove return air damper (Insulated Gloves) |  |  |  | Clean the coil with compressed air (Compressed Air) |  |  |  | Close HVAC components (None) |  |  | Sr. No. | Components Affected | [19 empty] | Remove Heat bank screws (Spanner)
[6 empty] | 1 | Air Blower Circuit Breakers |  | Open: 1, Close: 0 |  | Fault Reset Logic | [11 empty] | Check moisture indicator on the sight glass (1) to find any excessive moisture in the system. (Electronic Leak Detector) |  |  |  | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) |  |  |  | Unscrew bolt compressor unit cover (Spanner) |  |  | 1 | Heater Circuit Breaker |  | Open: 1, Close: 0 | [17 empty] | Remove Heat bank assembly (Insulated Gloves)
[7 empty] | Supply Air Blower | [15 empty] | Locate the leak and repair (Spanner) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) |  |  |  | Compressor Cover Removal (None) |  |  | 2 | Heater | [19 empty] | Replace Heat bank assembly (None)
[7 empty] | Fresh Air Damper | [15 empty] | Check working (Visual Inspection) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) |  |  |  | Check compressor of excessive noise or leaks (None) |  |  | 3 | RAT Sensor | [19 empty] | Clean Heat bank (Compressed Air Gun)
[27 empty] | Open supply air blower (Spanner) |  |  |  | Unscrew compressor bolt (Spanner) |  |  | 4 | Heater Circuit Breaker Manual Reset Required | [19 empty] | Secure the Heat bank screws (None)
[7 empty] | Cause 1 & Rectified | [19 empty] | Clean the supply air blower (1) with compressed air. (Compressed Air Gun) |  |  |  | Remove the compressor (Insulated Gloves) |  |  | 5 | Electrical Connections | [19 empty] | Run HVAC 20 mins. (None)
[7 empty] | Cause 2 & Rectified | [14 empty] | Sr. No. | Components Affected |  |  |  | Rotate supply air blower (1) motor with hand and ensure that only a light force is required to rotate it. (Insulated Hand Gloves) |  |  |  | Replace the compressor (None) | [23 empty] | Unusual noise from compressor assembly (None)
[7 empty] | Cause 3 & Rectified | [14 empty] | 1 | Condensor Fan Motor |  | Open: 1, Close: 0 |  | Remove supply air blower (Screwdriver) |  |  |  | Check hp lp pressure using manifold gauge set (None) |  |  |  | Cause 1 & Rectified | [19 empty] | Unscrew bolt compressor unit cover (Spanner)
[7 empty] | Fault Reset Logic |  | 1: Reset | [12 empty] | 2 | Condensor Fan Circuit Breaker |  |  |  | Replace supply air blower (Visual Inspection) |  |  |  | Unscrew Fan bolt (Spanner) |  |  |  | Cause 2 & Rectified | [19 empty] | Compressor Cover Removal (None)
[22 empty] | 3 | Condensor Coil |  |  |  | Close air supply blower (Visual Inspection) |  |  |  | Open fan cover (Insulated Gloves) |  |  |  | Cause 3 & Rectified | [19 empty] | Check hp lp pressure using manifold gauge set (None)
[22 empty] | 4 | Refrigerent Level |  |  |  | Unscrew bottom panel (Spanner) |  |  |  | Remove the compressor (Insulated Gloves) |  |  |  | Cause 4 & Rectified | [19 empty] | Compressor Cover close (None)
[27 empty] | Remove bottom panel (Insulated Gloves) |  |  |  | Replace the compressor (None) |  |  |  | Cause 5 & Rectified | [19 empty] | Screw bolt compressor unit cover (None)
[23 empty] | Cause 1 & Rectified |  |  |  | Unscrew return air damper (Spanner) |  |  |  | Close HVAC components (None) |  |  |  | Fault Reset Logic | [19 empty] | Unscrew bottom panel (Spanner)
[23 empty] | Cause 2 & Rectified |  |  |  | Remove return air damper (Insulated Gloves) |  |  |  | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner) | [23 empty] | Remove bottom panel (Insulated Gloves)
[23 empty] | Cause 3 & Rectified |  |  |  | Check moisture indicator on the sight glass (1) to find any excessive moisture in the system. (Electronic Leak Detector) |  |  |  | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers) | [23 empty] | Unscrew return air damper (Spanner)
[23 empty] | Cause 4 & Rectified |  |  |  | Locate the leak and repair (Spanner) |  |  |  | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None) | [23 empty] | Remove return air damper (Insulated Gloves)
[23 empty] | Fault Reset Logic |  |  |  | Unbolt the return air temperature sensor (Spanner) |  |  |  | Check temperature of solenoid valve using clamp thermometer (Clamp Thermometer) | [23 empty] | Unscrew Fan cover bolt (Spanner)
[27 empty] | Remove the return air temperature sensor (None) |  |  |  | Unscrew solenoid valve using spanner (Spanner) | [23 empty] | Open fan cover (Insulated Gloves)
[27 empty] | Replace the return air temperature sensor (None) |  |  |  | Remove solenoid valve (Visual Inspection) | [23 empty] | Clean the condenser fan with dry compressed air (Compressed Air)
[27 empty] | Secure the RAT sensor bolt (None) |  |  |  | Replace solenoid valve (Visual Inspection) | [23 empty] | Unscrew condenser fan bolt (Spanner)
[27 empty] | Check the temperature sensors for any damage (Clamp Thermometer) |  |  |  | Screw solenoid valve using spanner (Visual Inspection) | [23 empty] | Remove condenser fan (Insulated Gloves)
[27 empty] | Place external calibrated temperature sensor close to the return air temperature sensor. (Calibrated Thermometer) |  |  |  | Close HVAC components (None) | [23 empty] | Replace condenser fan (None)
[27 empty] | Check working (Visual Inspection) | [27 empty] | Close fan cover (None)
Secure Fan cover bolt (None)
[30 empty] | Sr. No. | Components Affected | [23 empty] | Run HVAC 20 mins. (None)
[26 empty] | Sr. No. | Components Affected |  |  | 1 | Refrigerent Level |  | Open: 1, Close: 0 | [21 empty] | Loosen and remove 24 nos M8X20 bolts (8) along with washer set (7) to open evaporator cover (9). (Spanner)
[26 empty] | 1 | Circuit Breaker |  | Open: 1, Close: 0 | 2 | Evaporator Coil | [23 empty] | Remove hinge pins to remove the evaporator cover (9) from HVAC unit. (Pliers)
[26 empty] | 2 | Condensor Fan Motor |  |  | 3 | TX Valve | [23 empty] | Remove the evaporator cover (9) from HVAC unit using suitable lifting device. (None)
[26 empty] | 3 | RAT Sensor |  |  | 4 | Condensor Coil | [23 empty] | Unusual noise from supply air blower (None)
[30 empty] | 5 | Compressor | [23 empty] | Open supply air cover (Spanner)
[27 empty] | Cause 1 & Rectified |  |  | 6 | Solenoid Valve | [23 empty] | Remove supply air blower (Screwdriver)
[27 empty] | Cause 2 & Rectified | [27 empty] | Replace supply air blower (Visual Inspection)
[27 empty] | Cause 3 & Rectified |  |  |  | Cause 1 & Rectified |  | Not preent | [21 empty] | Close supply air cover (None)
[27 empty] | Fault Reset Logic |  |  |  | Cause 2 & Rectified | [23 empty] | Check for leaks in TX Valve (Electronic Leak Detector)
[31 empty] | Cause 3 & Rectified | [23 empty] | Close the evaporator cover (None)
[31 empty] | Cause 4 & Rectified | [23 empty] | Fix hinge pins to close the evaporator cover (None)
[31 empty] | Cause 5 & Rectified | [23 empty] | Secure 24 nos M8X20 bolts (to close evaporator cover (None)
[31 empty] | Cause 6 & Rectified | [23 empty] | Remove Condenser Mesh with lifting device (Lifting Device)
[31 empty] | Fault Reset Logic | [23 empty] | Remove Condenser Coil & Filter with lifting device (Lifting Device)
Open Filter Drier Cover (Screwdriver)
Remove Filter Drier (Insulated Gloves)
Replace Filter Drier (Visual Inspection)
Close Filter Drier Cover (None)
Place Condenser Coil & Filter with lifting device (None)
Place Condenser Mesh with lifting device (None)
Run HVAC 20 mins. (None)
Unusual noise from HVAC Unit (None)
Tighten HVAC unit connection (Spanner)
Check working (None)
[54 empty] | Sr. No. | Components Affected
[54 empty] | 1 | Compressor |  | Open: 1, Close: 0
[54 empty] | 2 | Compresor Motor Heater Circuit Breaker
[54 empty] | 3 | Compresor Motor Heater Electrical Connections
[54 empty] | 4 | Compressor Bolts
[54 empty] | 5 | Refrigerent Level
[54 empty] | 6 | Condensor Fan Obstruction
[54 empty] | 7 | Supply Air Blower
[54 empty] | 8 | Filter Drier
[54 empty] | 9 | HVAC unit Component Bolts
Cause 1 & Rectified
Cause 2 & Rectified
Cause 3 & Rectified
Cause 4 & Rectified
Cause 5 & Rectified
Cause 6 & Rectified
Cause 7 & Rectified
Cause 8 & Rectified
Cause 9 & Rectified
Fault Reset Logic